## Input_guide
This guide explains how to properly format input data for power system modeling based on the provided system information template. The template is structured with multiple sections, each representing different components of a power system.
Template Structure
The Excel template contains the following main sections:
1 | cable | Cable
2 | xline | Transmission Line
3 | bus | Bus
4 | xform2w | 2-Winding-Transformer
5 | xform3w | 3-Winding-Transformer
6 | util | External Grid
7 | syngen | Synchronous Generator
8 | pvarray | Photovoltaic Array
9 | lumpedload | Lumped Load
10 | capacitor | Capacitor
11 | mgset | Rotary UPS
12 | hvcb | High Voltage Circuit Breaker
13 | dcbus | DC Bus
14 | dcimpedance | DC Impedance
15 | dclumpedload | DC Lumped Load
16 | dcconverter | DC Converter
17 | dccb | DC Circuit Breaker
18 | inverter | Inverter
19 | charger | Charger
20 | battery | Battery Storage System
Cable
Element | Meaning | Type | Example
Index | Index | Int | 4
ID | Name | String | Cable_3
FromBus | From Bus | String | Bus_3
ToBus | Frrom Bus | String | Bus_4
CableLengthUnit | Enter the length of the cable and select the unit from the list box Length Unit = 0 : unit = ft Length Unit = 1 : unit = mile Length Unit = 2 : unit = m Length Unit = 3 : unit = km | String | 2
InService | Wether in service | Bool | true
InServiceState | The State of equipment | String | As-Built
LengthValue | The Value of Length | String | 2000
OhmsPerLengthUnit | Select impedance units as ohms per unit length or ohms OhmsPerLengthUnit=0; Unit = ft OhmsPerLengthUnit = 1; Unit = mile OhmsPerLengthUnit = 2; Unit = m OhmsPerLengthUnit = 3; Unit = km | String | 2
OhmsPerLengthValue | With the selection of ohms per unit length, a length should also be designated | String | 2000
RPosValue | Positive sequence resistances at the base temperature, in ohms, or ohms per unit length, per conductor | String | 0.230000004
RZeroValue | Zero sequence resistances at the base temperature, in ohms, or ohms per unit length, per conductor | String | 0.365999997
XPosValue | Positive sequence reactance levels, in ohms or ohms per unit length, per conductor | String | 0.0529999994
XZeroValue | Zero sequence reactance levels, in ohms or ohms per unit length, per conductor | String | 0.135000005
YPosValue | Positive sequence admittance values from library in micro-Siemens, or micro-Siemens per unit length, for each conductor | String | 0
YZeroValue | Zero sequence admittance values from library in micro-Siemens, or micro-Siemens per unit length, for each conductor | String | 0
Transmission Line
Element | Meaning | Type | Example
Index | Sequence number | Int | 1
ID | Line identifier | String | XLINE_1165
ExtRef | External reference identifier | String | 0
FixedLoc | Fixed location flag | String | 0
OtiGUID | Unique identifier | String | {81A6EB80-9107-40EB-9EF0-9747EF0BBF66}
CloneGuid | Clone identifier | String | {00000000-0000-0000-0000-000000000000}
UseElementColor | Use element color flag | String | 0
Hidden | Hidden flag | String | 0
MetafileName | Graphic file name | String | aline1.emf
Orientation | Direction angle (degrees) | String | 270
SymbolSize | Symbol size | String | 0
SymbolType | Symbol type | String | ANSI
ServiceState | Service status code | String | 0
InheritedState | Inherited status code | String | 0
FromBus | Source bus name | String | BUS__1314
ToBus | Destination bus name | String | BUS__1418
ID (duplicate) | Line identifier (duplicate field) | String | XLINE_1
IID | Internal identifier number | Int | 1270
InService | Whether in operation | Bool | true
InServiceState | Operation status description | String | New
Length | Line length value | String | 50
LengthUnit | Length unit (0=ft, 1=mile, 2=m, 3=km) | String | 2
PerLength | Per unit length flag | String | 1
PerLengthUnit | Per unit length unit | String | 1
RPos | Positive sequence resistance value | String | 0.361
RZero | Zero sequence resistance value | String | 0.361
XPos | Positive sequence reactance value | String | 0.263
XZero | Zero sequence reactance value | String | 0.920
YPos | Positive sequence admittance value | String | 0
YZero | Zero sequence admittance value | String | 0
Bus
Element | Meaning | Type | Example
Index | Sequence number | Int | 1
ID | Bus identifier | String | Bus_1
OpVMag | Operating voltage magnitude (% of nominal) | String | 99.999946594
OpVAng | Operating voltage angle (degrees) | String | 6.5530657594e-05
UserDefinedPDGUID | User defined protection device GUID | String | ""
InService | Whether in operation | Bool | true
ServiceState | Service status code | String | 1
Area | Area number | String | 1
AsymmRMS | Asymmetrical RMS value | String | 0
BasekV | Base voltage in kV | String | 0
BusReferenceName | Bus reference name | String | 0
NominalkV | Nominal voltage in kV | String | 10
VMag | Initial voltage magnitude (% of nominal) | String | 100
VMaxLimit | Maximum voltage limit (% of nominal) | String | 105
VMinLimit | Minimum voltage limit (% of nominal) | String | 90
Zone | Zone number | String | 1
2-Winding-Transformer
Element | Meaning | Type | Example
Index | Sequence number | Int | 1
ID | Transformer identifier | String | XFOR_823
AnsiMaxMVA | ANSI maximum MVA rating | String | 50
AnsiMVA | ANSI MVA rating | String | 50
AnsiPosXR | ANSI positive sequence X/R ratio | String | 20
AnsiPosZ | ANSI positive sequence impedance | String | 10
AnsiZeroXoverR | ANSI zero sequence X/R ratio | String | 20
AnsiZeroZ | ANSI zero sequence impedance | String | 10
Buried | Buried flag | String | 0
VectorOrWinding | Vector or winding configuration | String | 1
PrimConnectionButton | Primary connection type | String | 1
SecConnectionButton | Secondary connection type | String | 0
PrimNeutralConn | Primary neutral connection | String | 1
SecNeutralConn | Secondary neutral connection | String | 1
CenterTap | Center tap flag | String | 0
PrimPercentTap | Primary percent tap setting | String | 0
SecPercentTap | Secondary percent tap setting | String | 0
PrimMaxPercentFixedTap | Primary maximum percent fixed tap | String | 5
PrimMinPercentFixedTap | Primary minimum percent fixed tap | String | -5
SecMaxPercentFixedTap | Secondary maximum percent fixed tap | String | 5
SecMinPercentFixedTap | Secondary minimum percent fixed tap | String | -5
PhaseShiftHL | Phase shift high-to-low | String | 0
PhaseShiftPS | Phase shift primary-to-secondary | String | 0
PhaseShiftType | Phase shift type | String | 0
FromBus | Primary side bus name | String | Bus_3
ToBus | Secondary side bus name | String | Bus_4
InService | Whether in operation | Bool | true
InServiceState | Operation status description | String | Build
PrimkV | Primary voltage in kV | String | 10
SeckV | Secondary voltage in kV | String | 0.8
ZBaseMVA | Base MVA for impedance values | String | 100
3-Winding-Transformer
Element | Meaning | Type | Example
Index | Sequence number | Int | 1
ID | Three-winding transformer identifier | String | XFOR_823
InService | Whether in operation | Bool | true
InServiceState | Operation status description | String | Build
PrimaryBus | Primary winding bus name | String | Bus_1
SecondaryBus | Secondary winding bus name | String | Bus_2
TeritiaryBus | Tertiary winding bus name | String | Bus_3
PrimkV | Primary voltage in kV | String | 10
SeckV | Secondary voltage in kV | String | 0.8
TerkV | Tertiary voltage in kV | String | 0.4
PrimPercentTap | Primary winding percent tap setting | String | 0
SecPercentTap | Secondary winding percent tap setting | String | 0
TerPercentTap | Tertiary winding percent tap setting | String | 0
PrimkVA | Primary winding rated capacity in kVA | String | 150
SeckVA | Secondary winding rated capacity in kVA | String | 150
TerkVA | Tertiary winding rated capacity in kVA | String | 150
PSPosZ | Primary-Secondary positive sequence impedance | String | 20
PSPosXoverR | Primary-Secondary positive sequence X/R ratio | String | 10
PTPosZ | Primary-Tertiary positive sequence impedance | String | 20
PTPosXoverR | Primary-Tertiary positive sequence X/R ratio | String | 10
STPosZ | Secondary-Tertiary positive sequence impedance | String | 20
STZeroXoverR | Secondary-Tertiary zero sequence X/R ratio | String | 10
External Grid
Element | Meaning | Type | Example
Index | Sequence number | Int | 1
ID | Generator identifier | String | U2
OpVAng | Operating voltage angle | String | 0
OpVMag | Operating voltage magnitude (% of nominal) | String | 100
OpMW | Operating active power in MW | String | 7806.89746
OpMvar | Operating reactive power in Mvar | String | 5903.29541
VoltagePercent0-9 | Voltage percentage settings (0-9) | String | 100
BalancedRadio | Balanced radio setting | String | 0
Bus | Connected bus name | String | Bus_60
EarthingType | Earthing type code | String | 0
GroundingConnection | Grounding connection code | String | 0
InService | Whether in operation | Bool | true
InServiceState | Operation status description | String | As-Built
kAsc1p | Single-phase short circuit current in kA | String | 40.8248291
kAsc3p | Three-phase short circuit current in kA | String | 40.8248291
KV | Rated voltage in kV | String | 10
MaxQ | Maximum reactive power limit in Mvar | String | 0
MinQ | Minimum reactive power limit in Mvar | String | 0
Mvar | Reactive power setpoint in Mvar | String | 0
MW | Active power setpoint in MW | String | 0
NegR | Negative sequence resistance | String | 10
NegX | Negative sequence reactance | String | 10
OnePhase | Single-phase fault contribution | String | 707106.812
OnePhaseXoverR | Single-phase X/R ratio | String | 1
Phase | Phase setting | String | 0
PhaseType | Phase type code | String | 5
PosR | Positive sequence resistance | String | 10
PosX | Positive sequence reactance | String | 10
ThreePhase | Three-phase fault contribution | String | 707106.812
ThreePhaseXoverR | Three-phase X/R ratio | String | 1
TypeOfUtility | Utility type code | String | 0
VoltageAngle | Voltage angle setpoint | String | 0
VoltageMagnitude | Voltage magnitude setpoint (% of nominal) | String | 100
ZeroR | Zero sequence resistance | String | 10
ZeroX | Zero sequence reactance | String | 10
PdeStatus | Generator control mode | String | Swing
Generator
Element | Meaning | Type | Example
Index | Sequence number | Int
ID | Generator identifier | String
Bus | Connected bus name | String
CalcFromCapability | Calculate from capability flag | String
CompoundExc | Compound excitation flag | String
CouplerRpm | Coupler rotations per minute | String
CouplerWR2 | Coupler inertia constant | String
Damping | Damping coefficient | String
Efficency | Generator efficiency | String
Eqp | Transient voltage behind quadrature axis reactance | String
ExcWithstandLimit | Excitation withstand limit | String
ExcWithstandTime | Excitation withstand time | String
GenerationCategory | Generation category code | String
GostScExciterType | GOST standard exciter type | String
IecExcitationType | IEC excitation type | String
Ikp | Peak short-circuit current | String
IncludePFMvarController | Include power factor/Mvar controller flag | String
Inertia | Inertia constant | String
InService | Whether in operation | Bool
InServiceState | Operation status description | String
KV | Rated voltage in kV | String
LoadRpm | Load rotations per minute | String
LoadWR2 | Load inertia constant | String
MachineType | Machine type code | String
MachineWR2 | Machine inertia constant | String
MVA | Rated apparent power in MVA | String
MW | Active power setpoint in MW | String
PG | Active power generation | String
PlotI2t | Plot I²t curve flag | String
PlotShortTime | Plot short-time curve flag | String
Poles | Number of poles | String
PowerFactor | Power factor | String
PrimConnectionButton | Primary connection type | String
PrimEarthingType | Primary earthing type | String
PrimGroundingType | Primary grounding type | String
PrimNeutralConn | Primary neutral connection | String
RadioButtons | Radio buttons setting | String
RatedLifeTime | Rated lifetime | String
RdcPercent | DC resistance percentage | String
ReactivePower | Reactive power setpoint | String
RealPower | Real power setpoint | String
RPM | Rotations per minute | String
S100 | 100% apparent power rating | String
S120 | 120% apparent power rating | String
Sbreak | Breaking apparent power | String
ScExciterType | Short circuit exciter type | String
ScGenType | Short circuit generator type | String
TDoublePrimeD0 | Subtransient time constant d-axis | String
TDoublePrimeQ0 | Subtransient time constant q-axis | String
TPrimeD0 | Transient time constant d-axis | String
TPrimeQ0 | Transient time constant q-axis | String
TypeOfGenerator | Generator type code | String
VoltageAngle | Voltage angle setpoint | String
VoltageMagnitude | Voltage magnitude setpoint | String
X0 | Zero sequence reactance | String
X1 | Positive sequence reactance | String
X2 | Negative sequence reactance | String
Xd | Direct axis synchronous reactance | String
XdDoublePrime | Direct axis subtransient reactance | String
XdPrime | Direct axis transient reactance | String
XOverR | X/R ratio | String
XOverR0 | Zero sequence X/R ratio | String
XOverR2 | Negative sequence X/R ratio | String
Xq | Quadrature axis synchronous reactance | String
XqDoublePrime | Quadrature axis subtransient reactance | String
XqPrime | Quadrature axis transient reactance | String
XTolerance | Reactance tolerance | String
PdeStatus | Generator control mode | String
PV Array
Element | Meaning | Type | Example
Index | Sequence number | Int | 1
ID | PV array identifier | String | PVA1
Bus | Connected bus name | String | dcBus_1
BVmpp | Maximum power point voltage temperature coefficient | String | 0
BVmppTemp | Reference temperature for BVmpp | String | 0
AIscTemp | Short circuit current temperature coefficient | String | 0.0548
BVoc | Open circuit voltage temperature coefficient | String | 0
BVocTemp | Reference temperature for BVoc | String | -0.362399995
DCGrounded | DC grounding flag | String | 0
DCGroundR | DC ground resistance | String | 0
DeltaIrradiance | Irradiance variation | String | 0.0500000007
EarthingType | Earthing type code | String | 5
ExternalL | External inductance | String | 0
ExternalR | External resistance | String | 0
GenerationCategory | Generation category code | String | EP8AA
Impp | Maximum power point current | String | 7.30000019
ImpUD | Maximum power point current user-defined | String | 0
InService | Whether in operation | Bool | true
InServiceState | Operation status description | String | As-Built
InverterIncluded | Inverter included flag | String | 0
Isc | Short circuit current | String | 7.96000004
IscUD | Short circuit current user-defined | String | 0
Issue | Issue code | String | 0
LibModified | Library modified flag | String | 0
MppTracker | Maximum power point tracker flag | String | 0
NOCTemp | Nominal operating cell temperature | String | 50.2000008
NumPanelParallel | Number of panels in parallel | String | 20
NumPanelSeries | Number of panels in series | String | 27
PhaseType | Phase type code | String | 0
PVAPower | PV array power rating | String | 219.876007
PVAPowerTol | PV array power tolerance | String | 0
RevCtrl | Revision control flag | String | 0
Revision | Revision number | String | 0
SCModel | Short circuit model code | String | 0
ValidEquipmentCable | Valid equipment cable flag | String | 0
Vmpp | Maximum power point voltage | String | 30.1200008
VmpUD | Maximum power point voltage user-defined | String | 0
Voc | Open circuit voltage | String | 36.0600014
VocUD | Open circuit voltage user-defined | String | 0
OutServiceYear | Out of service year | String | 2045/1/1
ProfileSector | Profile sector | String
PVAMFR | PV array manufacturer | String | A10Green Technology
PVAModel | PV array model | String | A10J-M60-220
PVANumCells | Number of cells per panel | String | 60
PVASize | PV array size | String | 220
PVAType | PV array type | String | Polycrystalline
PVAVDC | PV array DC voltage | String | 1
SingleYearForecastOpt | Single year forecast option | String | 0
UniformScalePQ | Uniform scale PQ flag | String | 1
FailureRate | Failure rate | String | 0.0030000000000000001
MTTR | Mean time to repair | String | 200
NoOfLoads | Number of loads | String | 0
OutageRate | Outage rate | String | 0.000136970004
OutageTime | Outage time | String | 43.7999992
PermFailureRate | Permanent failure rate | String | 0.0030000000000000001
ReplaceTime | Replacement time | String | 10
SpareAvail | Spare availability flag | String | 0
SwitchTime | Switching time | String | 200
Lumped Load
Element | Meaning | Type | Example
Index | Sequence number | Int | 1
ID | Load identifier | String | Lump3
OpMW | Operating active power in MW | String | 0
OpMvar | Operating reactive power in Mvar | String | 0
OpMWStLd | Operating active power of static load | String | 0
OpMvarStLd | Operating reactive power of static load | String | 0
GroundingAmp | Grounding amperage | String | 0
GroundingOhm | Grounding resistance in ohms | String | 0
GroundingType | Grounding type code | String | 0
Bus | Connected bus name | String | Bus_6
InService | Whether in operation | Bool | true
InServiceState | Operation status description | String | As-Built
KV | Rated voltage in kV | String | 10
LRC | Locked rotor current | String | 650
ModelType | Load model type | String | Conventional
MotorLoadPercent | Motor load percentage | String | 80
MTLoadPercent | Motor-transformer load percentage | String | 100
MVA | Rated apparent power in MVA | String | 470
NeutralConn | Neutral connection type | String | 0
PercentTotalLoad | Percentage of total system load | String | 0
PF | Power factor | String | 85
Phase | Phase setting | String | 0
PhaseA_MVA | Phase A apparent power in MVA | String | 0
PhaseB_MVA | Phase B apparent power in MVA | String | 0
PhaseC_MVA | Phase C apparent power in MVA | String | 0
PhaseConnection | Phase connection type | String | 0
StaticLoadPercent | Static load percentage | String | 20
TdP | Direct axis transient time constant | String | 0.2
X | Reactance | String | 150
XdP | Direct axis transient reactance | String | 23.0769
XOverR | X/R ratio | String | 6.67
XP | Transient reactance | String | 23.0769
XPP | Subtransient reactance | String | 15.3846
PdeStatus | Load control mode | String | Continuous
BasekV | Base voltage in kV | String | 0
LoadType | Load type code | String | 0
OutServiceYear | Out of service year | String | 52963
PhaseA_Amp | Phase A current in amperes | String | 0
PhaseA_PF | Phase A power factor | String | 0
PhaseB_Amp | Phase B current in amperes | String | 0
PhaseB_PF | Phase B power factor | String | 0
PhaseC_Amp | Phase C current in amperes | String | 0
PhaseC_PF | Phase C power factor | String | 0
Priority | Load priority level | String | 3
ProfileSector | Profile sector | String
SingleYearForecastOpt | Single year forecast option | String | 0
Ta | Armature time constant | String | 0
UDBasekV | User-defined base voltage in kV | String | 0
UniformScalePQ | Uniform scale PQ flag | String | 1
WR | Inertia constant | String | 0
DataStream | Data stream information | String | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA
FailureRate | Failure rate | String | 0
MTTR | Mean time to repair | String | 50
NoOfLoads | Number of loads | String | 1
OutageRate | Outage rate | String | 0.15
OutageTime | Outage time | String | 50
PermFailureRate | Permanent failure rate | String | 0.02
ReplaceTime | Replacement time | String | 10
SpareAvail | Spare availability flag | String | 0
SwitchTime | Switching time | String | 50
Capacitor
Element | Meaning | Type | Example
Index | Sequence number | Int
ID | Capacitor identifier | String
OpMW | Operating active power in MW | String
OpMvar | Operating reactive power in Mvar | String
InService | Whether in operation | Bool
InServiceState | Operation status description | String
InterDF | Interface definition flag | String
Phase | Phase setting | String
PhaseConnection | Phase connection type | String
PdeStatus | Capacitor control mode | String
CurrentLowerBand | Current lower threshold band | String
CurrentSwitchInValue | Current value to switch in | String
CurrentSwitchOutValue | Current value to switch out | String
CurrentUpperBand | Current upper threshold band | String
StepsPerBank | Number of steps per bank | String
TimeDelayType | Time delay type code | String
VoltageCtrlUnit | Voltage control unit | String
VoltageLowerBand | Voltage lower threshold band | String
VoltageSwitchInValue | Voltage value to switch in | String
VoltageSwitchOutValue | Voltage value to switch out | String
VoltageUpperBand | Voltage upper threshold band | String
FailureRate | Failure rate | String
MTTR | Mean time to repair | String
OutageRate | Outage rate | String
OutageTime | Outage time | String
PermFailureRate | Permanent failure rate | String
ReplaceTime | Replacement time | String
SpareAvail | Spare availability flag | String
SwitchTime | Switching time | String
UnitLength | Unit length | String
MgSet
Element | Meaning | Type | Example
Index | Sequence number | Int
ID | Motor-Generator set identifier | String
KV | Rated voltage in kV | String
MVA | Rated apparent power in MVA | String
X1 | Positive sequence reactance | String
Xdu | Direct axis unsaturated reactance | String
Xq | Quadrature axis synchronous reactance | String
XqP | Quadrature axis transient reactance | String
XqPP | Quadrature axis subtransient reactance | String
Xqu | Quadrature axis unsaturated reactance | String
FailureRate | Failure rate | String
MTTR | Mean time to repair | String
NoOfLoads | Number of loads | String
OutageRate | Outage rate | String
OutageTime | Outage time | String
PermFailureRate | Permanent failure rate | String
ReplaceTime | Replacement time | String
SpareAvail | Spare availability flag | String
SwitchTime | Switching time | String
UnitLength | Unit length | String
High Voltage Circuit Breaker
Element | Meaning | Type | Example
Index | Sequence number | Int
ID | Circuit breaker identifier | String
FromElement | Starting connection element | String
ToElement | Ending connection element | String
FailureRate | Failure rate | String
MTTR | Mean time to repair | String
OutageRate | Outage rate | String
OutageTime | Outage time | String
PermFailureRate | Permanent failure rate | String
PdeStatus | Circuit breaker control mode | String | Closed/Open
ReplaceTime | Replacement time | String
SpareAvail | Spare availability flag | String
SwitchTime | Switching time | String
DC Bus
Element | Meaning | Type | Example
Index | Sequence number | Int | 1
ID | DC Bus identifier | String | dcBus_1
InService | Whether in operation | Bool | true
InServiceState | Operation status description | String | As-Built
MaxLoadFactor | Maximum load factor in percent | String | 125
MinLoadFactor | Minimum load factor in percent | String | 80
NominalV | Nominal voltage in volts | String | 824
PhaseType | Phase type code | String | 0
WireType | Wire type code | String | 1
aCoefficient | Alpha coefficient | String | 100
FailureRate | Failure rate | String | 0
MTTR | Mean time to repair | String | 0
NoOfLoads | Number of loads | String | 1
OutageRate | Outage rate | String | 0
OutageTime | Outage time | String | 0
PermFailureRate | Permanent failure rate | String | 0
ReplaceTime | Replacement time | String | 0
SpareAvail | Spare availability flag | String | 0
SwitchTime | Switching time | String | 0
UnitLength | Unit length | String | 0
DC Impedance
Element | Meaning | Type | Example
Index | Sequence number | Int | 1
ID | DC Impedance identifier | String | dcZ1
FromBus | Starting bus connection | String | dcBus_1
IID | Internal identifier | String | 3222
InService | Whether in operation | Bool | true
InServiceState | Operation status description | String | As-Built
RValue | Resistance value in ohms | String | 0.06
LValue | Inductance value | String | 0
ToBus | Ending bus connection | String | dcBus_2
PhaseType | Phase type code | String | 0
WireType | Wire type code | String | 1
FailureRate | Failure rate | String | 0
MomentaryRate | Momentary failure rate | String | 80
MTTR | Mean time to repair | String | 0
NoOfLoads | Number of loads | String | 1
OutageRate | Outage rate | String | 0
OutageTime | Outage time | String | 0
PermFailureRate | Permanent failure rate | String | 0
ReplaceTime | Replacement time | String | 0
SpareAvail | Spare availability flag | String | 0
SwitchTime | Switching time | String | 0
UnitLength | Unit length | String | 0
DC Lumped Load
Element | Meaning | Type | Example
Index | Sequence number | Int | 1
ID | DC Lumped Load identifier | String | dcLump2
DCV | DC voltage in volts | String | 824
InService | Whether in operation | Bool | true
InServiceState | Operation status description | String | As-Built
KFactor | K factor | String | 1000
KW | Power in kilowatts | String | 150
MTLoadPercent | Motor-transformer load percentage | String | 100
Bus | Connected bus name | String | dcBus6
StaticLoadPercent | Static load percentage | String | 0
PhaseType | Phase type code | String | 0
ProfileSector | Profile sector | String
SingleYearForecastOpt | Single year forecast option | String | 0
FailureRate | Failure rate | String | 0
MTTR | Mean time to repair | String | 0
NoOfLoads | Number of loads | String | 1
OutageRate | Outage rate | String | 0
OutageTime | Outage time | String | 0
PermFailureRate | Permanent failure rate | String | 0
ReplaceTime | Replacement time | String | 0
SpareAvail | Spare availability flag | String | 0
SwitchTime | Switching time | String | 0
UniformScalePQ | Uniform scale PQ flag | String | 0
DC Converter
Element | Meaning | Type | Example
Index | Sequence number | Int
ID | DC Converter identifier | String
IMaxPercent | Maximum current percentage | String
InputBus | Input bus connection | String
InputPhaseType | Input phase type code | String
InputTerminalType | Input terminal type | String
InputV | Input voltage | String
InService | Whether in operation | Bool
InServiceState | Operation status description | String
KW | Power rating in kilowatts | String
OutputBus | Output bus connection | String
OutputPhaseType | Output phase type code | String
OutputTap | Output tap setting | String
OutputTerminalType | Output terminal type | String
OutputV | Output voltage | String
PercentEFF | Efficiency percentage | String
FailureRate | Failure rate | String
MTTR | Mean time to repair | String
OutageRate | Outage rate | String
OutageTime | Outage time | String
PermFailureRate | Permanent failure rate | String
ReplaceTime | Replacement time | String
SpareAvail | Spare availability flag | String
SwitchTime | Switching time | String
DC Circuit Breaker
Element | Meaning | Type | Example
Index | Sequence number | Int
ID | DC Circuit Breaker identifier | String
FromBus | Starting bus connection | String
ToBus | Ending bus connection | String
FailureRate | Failure rate | String
MTTR | Mean time to repair | String
OutageRate | Outage rate | String
OutageTime | Outage time | String
PdeStatus | Circuit breaker status | String
PermFailureRate | Permanent failure rate | String
ReplaceTime | Replacement time | String
SpareAvail | Spare availability flag | String
SwitchTime | Switching time | String
Inverter
Element | Meaning | Type | Example
Index | Sequence number | Int | 1
ID | Inverter identifier | String | Inv2
OpAcKw | Operating AC power in kW | String | 0
OpAcKvar | Operating AC reactive power | String | 0
OpAcKv | Operating AC voltage in kV | String | 0
OpAcAmp | Operating AC current in amps | String | 0
OpDcKw | Operating DC power in kW | String | 0
DckW | DC power rating in kW | String | 0
DcPercentEFF | DC efficiency percentage | String | 90
DcPercentIMax | Maximum DC current percentage | String | 105
DcPhaseType | DC phase type code | String | 0
DcTerminalType | DC terminal type | String | 1
DcV | DC voltage rating | String | 824
DcVMax | Maximum DC voltage | String | 110
DcVMin | Minimum DC voltage | String | 0
diDV | Current-voltage slope | String | 2
EarthingType | Earthing/grounding type | String | 0
GenerationCategory | Generation category data | String | IP8AAPP/AAA...
BusID | AC bus identifier | String | Bus_20
CZNetwork | DC bus identifier | String | dcBus_1
IkPFMax | Maximum power factor current | String | 110
IkPFMin | Minimum power factor current | String | 100
IMin | Minimum current | String | 100
InService | Whether in operation | Bool | false
ParentName | Parent equipment name | String
InServiceState | Operation status description | String | As-Built
KV | AC voltage rating in kV | String | 10
GenCat0ACkW | Generation category AC power | String | 100
GenCat0kVar | Generation category reactive power | String | 50
KVA | Apparent power rating | String | 0
KVAMax | Maximum apparent power | String | 300
KvarMax | Maximum reactive power | String | 0
KWMax | Maximum active power | String | 0
MaxPF | Maximum power factor | String | 100
MinPF | Minimum power factor | String | 80
MPPTControl | Maximum power point tracking control | String | 0
MPPTDCVMax | MPPT maximum DC voltage | String | 110
MPPTDCVMin | MPPT minimum DC voltage | String | 40
MPPTInitialDCV | MPPT initial DC voltage | String | 100
MPPTNumSteps | MPPT number of steps | String | 15
MvarLimitsOpt | Reactive power limits option | String | 0
NegSeqCurrentInjection | Negative sequence current injection | String | 0
NegSeqCurrentLimit | Negative sequence current limit | String | 100
NegSeqDeadbandMin | Negative sequence deadband minimum | String | 10
NegSeqDiDV | Negative sequence current-voltage slope | String | 2
PF | Power factor | String | 100
Phase | Phase code | String | 0
PhaseConnection | Phase connection code | String | 0
Charger
Element | Meaning | Type | Example
Index | Sequence number | Int
ID | Rectifier identifier | String
OpMW | Operating active power in MW | String
OpMvar | Operating reactive power in Mvar | String
DckW | DC power rating in kW | String
DcLoadkW | DC load power in kW | String
DcPercentIMax | Maximum DC current percentage | String
DcPhaseType | DC phase type code | String
DcSmoothL | DC smoothing inductance | String
DcSmoothR | DC smoothing resistance | String
DcTapPercentage | DC tap percentage | String
DcTerminalType | DC terminal type | String
DcV | DC voltage rating | String
DcVeq | DC equivalent voltage | String
DcVFloat | DC float voltage | String
DcVFloatMax | Maximum DC float voltage | String
DcVFloatMin | Minimum DC float voltage | String
IAtZeroV | Current at zero voltage | String
IMin | Minimum current | String
InService | Whether in operation | Bool
InServiceState | Operation status description | String
Iop | Operating current | String
Issue | Issue code or description | String
KV | AC voltage rating in kV | String
KVA | Apparent power rating in kVA | String
MVA | Apparent power rating in MVA | String
Bus | AC bus identifier | String
CZNetwork | DC bus identifier | String
MVASc | Short circuit MVA | String
OperatingAlfa | Operating firing angle | String
PercentDF | Derating factor percentage | String
PercentEFF | Efficiency percentage | String
Phase | Phase code | String
PhaseConnection | Phase connection code | String
ScContribution | Short circuit contribution | String
ScK | Short circuit constant | String
SP3Wire | Three-wire option | String
SpareDF | Spare data field | String
SystemR | System resistance | String
SystemX | System reactance | String
SystemXOverR | System X/R ratio | String
UpdateZFromSc | Update impedance from short circuit | String
VAtIMax | Voltage at maximum current | String
Xc | Commutation reactance | String
Battery
Element | Meaning | Type | Example
Index | Sequence number | Int | 1
ID | Battery identifier | String | Battery1
BatteryType | Battery technology type | String | 0
DisChargeMethod | Discharge method code | String | 1
Eff | Efficiency percentage | String | 85
IchargeMax | Maximum charging current | String | 10
IdischargeMax | Maximum discharging current | String | 20
InService | Whether in operation | Bool | false
InServiceState | Operation status description | String | As-Built
Bus | Connected DC bus identifier | String | dcBus_3
NrOfCells | Number of cells | String | 20
NoOfPacks | Number of battery packs | String | 20
NrOfStrings | Number of parallel strings | String | 20
IValue | Current value | String | 0
OperatingSoC | Operating state of charge | String | 0
OpGenBusGID | Operating generator bus global ID | String | 2185560065
OpGenBusID | Operating generator bus ID | String | 3220
OpGenChargeBand | Operating generator charge band | String | 0.001
OpGenChargeMW | Operating generator charge power in MW | String | 1
OpGenDisChargeBand | Operating generator discharge band | String | 0.001
OpGenDisChargeMW | Operating generator discharge power in MW | String | 0.1
PhaseType | Phase type code | String | 0
QValue | Reactive power value | String | 110
Rated | Rated capacity indicator | String | 1
TerminalType | Terminal type | String | 1
VbatMax | Maximum battery voltage | String | 120
VbatMin | Minimum battery voltage | String | 100
FailureRate | Failure rate | String | 0
MTTR | Mean time to repair | String | 0
OutageRate | Outage rate | String | 0
OutageTime | Outage time | String | 0
PermFailureRate | Permanent failure rate | String | 0
ReplaceTime | Replacement time | String | 0
SpareAvail | Spare availability flag | String | 0
SwitchTime | Switching time | String | 0
ModelID | Battery model identifier | String | 450043002D...
ModelType | Battery model type | String | 050000000000...

## cable
Index | ID | FromBus | ToBus | CableLengthUnit | InService | InServiceState | LengthValue | OhmsPerLengthUnit | OhmsPerLengthValue | RPosValue | RZeroValue | XPosValue | XZeroValue | YPosValue | YZeroValue
1 | Cable1 | Bus_2 | Bus_1 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.230000004 | 0.365999997 | 0.0529999994 | 0.135000005 | 0 | 0
2 | Cable2 | Bus_3 | Bus_2 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.230000004 | 0.365999997 | 0.0529999994 | 0.135000005 | 0 | 0
3 | Cable3 | Bus_4 | Bus_3 | 2 | true | As-Built | 500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
4 | Cable4 | Bus_5 | Bus_4 | 2 | true | As-Built | 2000 | 2 | 1000 | 0.230000004 | 0.365999997 | 0.0529999994 | 0.135000005 | 0 | 0
5 | Cable5 | Bus_5 | Bus_6 | 2 | true | As-Built | 3000 | 2 | 1000 | 0.230000004 | 0.365999997 | 0.0529999994 | 0.135000005 | 0 | 0
6 | Cable6 | Bus_6 | Bus_7 | 2 | true | As-Built | 1200 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
7 | Cable7 | Bus_7 | Bus_8 | 2 | true | As-Built | 800 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
8 | Cable8 | Bus_9 | Bus_5 | 2 | true | As-Built | 750 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
9 | Cable9 | Bus_10 | Bus_9 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
10 | Cable10 | Bus_10 | Bus_11 | 2 | true | As-Built | 200 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
11 | Cable11 | Bus_11 | Bus_12 | 2 | true | As-Built | 1500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
12 | Cable12 | Bus_12 | Bus_13 | 2 | true | As-Built | 400 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
13 | Cable13 | Bus_13 | Bus_14 | 2 | true | As-Built | 1080 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
14 | Cable14 | Bus_15 | Bus_11 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
15 | Cable59 | Bus_16 | Bus_15 | 2 | true | As-Built | 1300 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
16 | Cable15 | Bus_17 | Bus_16 | 2 | true | As-Built | 1100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
17 | Cable16 | Bus_18 | Bus_17 | 2 | true | As-Built | 1600 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
18 | Cable62 | Bus_19 | Bus_18 | 2 | true | As-Built | 1100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
19 | Cable63 | Bus_20 | Bus_19 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
20 | Cable72 | Bus_21 | Bus_18 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
21 | Cable65 | Bus_22 | Bus_23 | 2 | true | As-Built | 1350 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
22 | Cable64 | Bus_23 | Bus_24 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
23 | Cable17 | Bus_24 | Bus_19 | 2 | true | As-Built | 2100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
24 | Cable66 | Bus_25 | Bus_23 | 2 | true | As-Built | 1500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
25 | Cable67 | Bus_26 | Bus_25 | 2 | true | As-Built | 1080 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
26 | Cable68 | Bus_27 | Bus_25 | 2 | true | As-Built | 1500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
27 | Cable69 | Bus_28 | Bus_27 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
28 | Cable70 | Bus_29 | Bus_27 | 2 | true | As-Built | 1100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
29 | Cable61 | Bus_30 | Bus_29 | 2 | true | As-Built | 1100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.0270000007 | 0 | 0
30 | Cable71 | Bus_31 | Bus_29 | 2 | true | As-Built | 800 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
31 | Cable20 | Bus_32 | Bus_31 | 2 | true | As-Built | 120 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
32 | Cable21 | Bus_32 | Bus_33 | 2 | true | As-Built | 2000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
33 | Cable22 | Bus_33 | Bus_34 | 2 | true | As-Built | 1320 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
34 | Cable23 | Bus_34 | Bus_35 | 2 | true | As-Built | 1650 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
35 | Cable24 | Bus_35 | Bus_36 | 2 | true | As-Built | 1100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
36 | Cable25 | Bus_37 | Bus_36 | 2 | true | As-Built | 1350 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
37 | Cable26 | Bus_36 | Bus_38 | 2 | true | As-Built | 950 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
38 | Cable27 | Bus_38 | Bus_39 | 2 | true | As-Built | 1800 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
39 | Cable58 | Bus_35 | Bus_40 | 2 | true | As-Built | 2500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
40 | Cable56 | Bus_40 | Bus_41 | 2 | true | As-Built | 1600 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
41 | Cable55 | Bus_41 | Bus_42 | 2 | true | As-Built | 1350 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
42 | Cable54 | Bus_42 | Bus_43 | 2 | true | As-Built | 1400 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
43 | Cable53 | Bus_43 | Bus_44 | 2 | true | As-Built | 950 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
44 | Cable52 | Bus_44 | Bus_45 | 2 | true | As-Built | 1350 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
45 | Cable50 | Bus_45 | Bus_46 | 2 | true | As-Built | 800 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.0900000036 | 0 | 0
46 | Cable43 | Bus_46 | Bus_47 | 2 | true | As-Built | 190 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
47 | Cable42 | Bus_47 | Bus_48 | 2 | true | As-Built | 1100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
48 | Cable41 | Bus_48 | Bus_49 | 2 | true | As-Built | 1160 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
49 | Cable39 | Bus_49 | Bus_50 | 2 | true | As-Built | 450 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
50 | Cable37 | Bus_51 | Bus_50 | 2 | true | As-Built | 1405 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
51 | Cable36 | Bus_52 | Bus_51 | 2 | true | As-Built | 970 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.0900000036 | 0 | 0
52 | Cable35 | Bus_53 | Bus_52 | 2 | true | As-Built | 1180 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
53 | Cable34 | Bus_54 | Bus_53 | 2 | true | As-Built | 1200 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
54 | Cable33 | Bus_55 | Bus_54 | 2 | true | As-Built | 1360 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
55 | Cable32 | Bus_56 | Bus_55 | 2 | true | As-Built | 1400 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
56 | Cable31 | Bus_57 | Bus_56 | 2 | true | As-Built | 1130 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
57 | Cable30 | Bus_58 | Bus_57 | 2 | true | As-Built | 1360 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
58 | Cable29 | Bus_59 | Bus_58 | 2 | true | As-Built | 900 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
59 | Cable28 | Bus_60 | Bus_59 | 2 | true | As-Built | 1700 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
60 | Cable38 | Bus_53 | Bus_61 | 2 | true | As-Built | 1500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
61 | Cable40 | Bus_49 | Bus_51 | 2 | true | As-Built | 1300 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
62 | Cable51 | Bus_62 | Bus_45 | 2 | true | As-Built | 1450 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
63 | Cable49 | Bus_63 | Bus_62 | 2 | true | As-Built | 1150 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
64 | Cable45 | Bus_64 | Bus_63 | 2 | true | As-Built | 1350 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
65 | Cable44 | Bus_65 | Bus_64 | 2 | true | As-Built | 200 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
66 | Cable46 | Bus_63 | Bus_66 | 2 | true | As-Built | 1500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
67 | Cable47 | Bus_66 | Bus_67 | 2 | true | As-Built | 1300 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
68 | Cable48 | Bus_67 | Bus_68 | 2 | true | As-Built | 1600 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
69 | Cable57 | Bus_69 | Bus_41 | 2 | true | As-Built | 1300 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
70 | Cable60 | Bus_70 | Bus_16 | 2 | true | As-Built | 800 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
71 | Cable18 |  |  | 0 | true | As-Built | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
72 | Cable19 |  |  | 0 | true | As-Built | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | c

## xline
Index | ID | ExtRef | FixedLoc | OtiGUID | CloneGuid | UseElementColor | Hidden | MetafileName | Orientation | SymbolSize | SymbolType | ServiceState | InheritedState | FromBus | ToBus | ID | IID | InService | InServiceState | Length | LengthUnit | PerLength | PerLengthUnit | RPos | RZero | XPos | XZero | YPos | YZero

## bus
Index | ID | OpVMag | OpVAng | UserDefinedPDGUID | InService | ServiceState | Area | AsymmRMS | BasekV | BusReferenceName | NominalkV | VMag | VMaxLimit | VMinLimit | Zone
1 | Bus_1 | 99.999946594 | 6.5530657594e-05 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
2 | Bus_2 | 98.5651245 | 0.197909728 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
3 | Bus_3 | 97.1315155 | 0.401596546 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
4 | Bus_4 | 96.8529129 | 0.306946069 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
5 | Bus_5 | 94.4161377 | 0.640870094 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
6 | Bus_6 | 94.0812225 | 0.710090518 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
7 | Bus_7 | 94.0812225 | 0.710090518 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
8 | Bus_8 | 94.0812225 | 0.710090518 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
9 | Bus_9 | 94.0822296 | 0.519215643 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
10 | Bus_10 | 93.8006897 | 0.401414156 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
11 | Bus_11 | 93.7444229 | 0.377768993 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
12 | Bus_12 | 93.6999893 | 0.365382254 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
13 | Bus_13 | 93.6936874 | 0.363624305 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
14 | Bus_14 | 93.6936874 | 0.363624305 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
15 | Bus_15 | 93.4929504 | 0.267430007 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
16 | Bus_16 | 93.1665649 | 0.12309961 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
17 | Bus_17 | 92.8908539 | 0.000182318938 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
18 | Bus_18 | 92.5413589 | -0.165451795 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
19 | Bus_19 | 92.3591995 | -0.264542699 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
20 | Bus_20 | 92.3591995 | -0.264542699 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
21 | Bus_21 | 92.5527115 | -0.161438063 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
22 | Bus_22 | 91.8473434 | -0.545909941 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
23 | Bus_23 | 91.8473434 | -0.545909941 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
24 | Bus_24 | 92.0122147 | -0.454804391 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
25 | Bus_25 | 91.6004715 | -0.683182716 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
26 | Bus_26 | 91.6004715 | -0.683182716 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
27 | Bus_27 | 91.3541183 | -0.821196556 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
28 | Bus_28 | 91.3541183 | -0.821196556 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
29 | Bus_29 | 91.1738052 | -0.922880352 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
30 | Bus_30 | 91.1738052 | -0.922880352 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
31 | Bus_31 | 91.0428543 | -0.997084975 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
32 | Bus_32 | 91.0232239 | -1.00823402 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
33 | Bus_33 | 90.7073517 | -1.19162476 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
34 | Bus_34 | 90.5423203 | -1.30090308 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
35 | Bus_35 | 90.3902359 | -1.42242289 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
36 | Bus_36 | 90.3758545 | -1.42657912 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
37 | Bus_37 | 90.3758545 | -1.42657912 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
38 | Bus_38 | 90.3634415 | -1.4301697 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
39 | Bus_39 | 90.3399048 | -1.43697548 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
40 | Bus_40 | 90.2258301 | -1.58826625 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
41 | Bus_41 | 90.178566 | -1.67796326 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
42 | Bus_42 | 90.1579971 | -1.74814987 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
43 | Bus_43 | 90.156662 | -1.81519425 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
44 | Bus_44 | 90.1558304 | -1.86068976 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
45 | Bus_45 | 90.1744766 | -1.91960502 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
46 | Bus_46 | 90.295372 | -1.92284822 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
47 | Bus_47 | 90.3258514 | -1.92310798 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
48 | Bus_48 | 90.5022736 | -1.92460775 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
49 | Bus_49 | 90.8308792 | -1.88516545 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
50 | Bus_50 | 90.8513412 | -1.88810778 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
51 | Bus_51 | 91.200676 | -1.81547654 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
52 | Bus_52 | 91.7180176 | -1.71431065 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
53 | Bus_53 | 92.4580078 | -1.56177747 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
54 | Bus_54 | 93.2112122 | -1.40914381 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
55 | Bus_55 | 94.108757 | -1.2272296 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
56 | Bus_56 | 95.0798569 | -1.03096819 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
57 | Bus_57 | 96.1256866 | -0.804962516 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
58 | Bus_58 | 97.430275 | -0.527751625 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
59 | Bus_59 | 98.3093948 | -0.344511449 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
60 | Bus_60 | 99.9999313 | -0.000167105711 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
61 | Bus_61 | 92.4580078 | -1.56177747 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
62 | Bus_62 | 89.9754791 | -1.97711182 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
63 | Bus_63 | 89.8583298 | -2.01106381 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
64 | Bus_64 | 89.834671 | -2.01794648 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
65 | Bus_65 | 89.834671 | -2.01794648 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
66 | Bus_66 | 89.7520599 | -2.04192042 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
67 | Bus_67 | 89.6599808 | -2.06872225 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
68 | Bus_68 | 89.6019821 | -2.08562732 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
69 | Bus_69 | 90.1601181 | -1.68330979 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
70 | Bus_70 | 93.1665649 | 0.12309961 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
71 | Bus_71 | 0 | 0 |  | true | 1 | 1 | 0 | 0 | 0 | 0 | 100 | 105 | 90 | 1
72 | Bus_72 | 0 | 0 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
73 | Bus_73 | 0 | 0 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1

## xform2w
Index | ID | AnsiMaxMVA | AnsiMVA | AnsiPosXR | AnsiPosZ | AnsiZeroXoverR | AnsiZeroZ | Buried | VectorOrWinding | PrimConnectionButton | SecConnectionButton | PrimNeutralConn | SecNeutralConn | CenterTap | PrimPercentTap | SecPercentTap | PrimMaxPercentFixedTap | PrimMinPercentFixedTap | SecMaxPercentFixedTap | SecMinPercentFixedTap | PhaseShiftHL | PhaseShiftPS | PhaseShiftType | FromBus | ToBus | InService | InServiceState | PrimkV | SeckV | ZBaseMVA

## xform3w
Index | ID | InService | InServiceState | PrimaryBus | SecondaryBus | TeritiaryBus | PrimkV | SeckV | TerkV | PrimPercentTap | SecPercentTap | TerPercentTap | PrimkVA | SeckVA | TerkVA | PSPosZ | PSPosXoverR | PTPosZ | PTPosXoverR | STPosZ | STZeroXoverR

## util
Index | ID | OpVAng | OpVMag | OpMW | OpMvar | VoltagePercent0 | VoltagePercent1 | VoltagePercent2 | VoltagePercent3 | VoltagePercent4 | VoltagePercent5 | VoltagePercent6 | VoltagePercent7 | VoltagePercent8 | VoltagePercent9 | BalancedRadio | Bus | EarthingType | GroundingConnection | InService | InServiceState | kAsc1p | kAsc3p | KV | MaxQ | MinQ | Mvar | MW | NegR | NegX | OnePhase | OnePhaseXoverR | Phase | PhaseType | PosR | PosX | ThreePhase | ThreePhaseXoverR | TypeOfUtility | VoltageAngle | VoltageMagnitude | ZeroR | ZeroX | PdeStatus
1 | U2 | 0 | 100 | 7806.89746 | 5903.29541 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | Bus_60 | 0 | 0 | true | As-Built | 40.8248291 | 40.8248291 | 10 | 0 | 0 | 0 | 0 | 10 | 10 | 707106.812 | 1 | 0 | 5 | 10 | 10 | 707106.812 | 1 | 0 | 0 | 100 | 10 | 10 | Swing
2 | U1 | 0 | 100 | 5690.04883 | 2804.14185 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | Bus_1 | 0 | 0 | true | As-Built | 40.8248291 | 40.8248291 | 10 | 0 | 0 | 0 | 0 | 10 | 10 | 707106.812 | 1 | 0 | 5 | 10 | 10 | 707106.812 | 1 | 0 | 0 | 100 | 10 | 10 | Swing

## syngen
Index | ID | Bus | CalcFromCapability | CompoundExc | CouplerRpm | CouplerWR2 | Damping | Efficency | Eqp | ExcWithstandLimit | ExcWithstandTime | GenerationCategory | GostScExciterType | IecExcitationType | Ikp | IncludePFMvarController | Inertia | InService | InServiceState | KV | LoadRpm | LoadWR2 | MachineType | MachineWR2 | MVA | MW | PG | PlotI2t | PlotShortTime | Poles | PowerFactor | PrimConnectionButton | PrimEarthingType | PrimGroundingType | PrimNeutralConn | RadioButtons | RatedLifeTime | RdcPercent | ReactivePower | RealPower | RPM | S100 | S120 | Sbreak | ScExciterType | ScGenType | TDoublePrimeD0 | TDoublePrimeQ0 | TPrimeD0 | TPrimeQ0 | TypeOfGenerator | VoltageAngle | VoltageMagnitude | X0 | X1 | X2 | Xd | XdDoublePrime | XdPrime | XOverR | XOverR0 | XOverR2 | Xq | XqDoublePrime | XqPrime | XTolerance | PdeStatus

## pvarray
Index | ID | Bus | BVmpp | BVmppTemp | AIscTemp | BVoc | BVocTemp | DCGrounded | DCGroundR | DeltaIrradiance | EarthingType | ExternalL | ExternalR | GenerationCategory | Impp | ImpUD | InService | InServiceState | InverterIncluded | Isc | IscUD | Issue | LibModified | MppTracker | NOCTemp | NumPanelParallel | NumPanelSeries | PhaseType | PVAPower | PVAPowerTol | RevCtrl | Revision | SCModel | ValidEquipmentCable | Vmpp | VmpUD | Voc | VocUD | OutServiceYear | ProfileSector | PVAMFR | PVAModel | PVANumCells | PVASize | PVAType | PVAVDC | SingleYearForecastOpt | UniformScalePQ | FailureRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime
1 | PVA1 | dcBus_1 | 0 | 0 | 0.0548 | 0 | -0.362399995 | 0 | 0 | 0.0500000007 | 5 | 0 | 0 | EP8AAPD/AAAKAAAA6AMAAAAAyEEBAHtCUnftQoQDAAAAAPBBZ+Z/QvtK0UIgAwAAAADwQc3McEKS6rhCvAIAAAAA8EE0s2FCW7CgQlgCAAAAAPBBmplSQtahiEL0AQAAAADwQQCAQ0KyjGFCkAEAAAAA8EFmZjRCdlAyQiwBAAAAAPBBzUwlQkGuA0LIAAAAAADwQTMzFkJZtqtBZAAAAAAA8EGaGQdCPRwlQQ | 7.30000019 | 0 | true | As-Built | 0 | 7.96000004 | 0 | 0 | 0 | 0 | 50.2000008 | 20 | 27 | 0 | 219.876007 | 0 | 0 | 0 | 0 | 0 | 30.1200008 | 0 | 36.0600014 | 0 | 2045/1/1 |  | A10Green Technology | A10J-M60-220 | 60 | 220 | Polycrystalline | 1 | 0 | 1 | 0.0030000000000000001 | 200 | 0 | 0.000136970004 | 43.7999992 | 0.0030000000000000001 | 10 | 0 | 200

## lumpedload
Index | ID | OpMW | OpMvar | OpMWStLd | OpMvarStLd | GroundingAmp | GroundingOhm | GroundingType | Bus | InService | InServiceState | KV | LRC | ModelType | MotorLoadPercent | MTLoadPercent | MVA | NeutralConn | PercentTotalLoad | PF | Phase | PhaseA_MVA | PhaseB_MVA | PhaseC_MVA | PhaseConnection | StaticLoadPercent | TdP | X | XdP | XOverR | XP | XPP | PdeStatus | BasekV | LoadType | OutServiceYear | PhaseA_Amp | PhaseA_PF | PhaseB_Amp | PhaseB_PF | PhaseC_Amp | PhaseC_PF | Priority | ProfileSector | SingleYearForecastOpt | Ta | UDBasekV | UniformScalePQ | WR | DataStream | FailureRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime
1 | Lump3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_6 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 470 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
2 | Lump6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_13 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 150 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
3 | Lump5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_12 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 132 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
4 | Lump14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_39 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
5 | Lump34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_59 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 160 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
6 | Lump33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_58 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 160 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
7 | Lump32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_57 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 315 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
8 | Lump31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_56 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 2230 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 10 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
9 | Lump30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_55 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 315 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
10 | Lump29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_54 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 300 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
11 | Lump28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_52 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 870 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
12 | Lump27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_50 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 1875 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 10 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
13 | Lump26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_49 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 430 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
14 | Lump25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_48 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 1130 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
15 | Lump24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_46 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 85 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
16 | Lump21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_64 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 160 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
17 | Lump23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_68 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 330 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
18 | Lump22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_67 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 315 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
19 | Lump20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_63 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 123 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
20 | Lump19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_62 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 323 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
21 | Lump18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_44 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 134 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
22 | Lump17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_42 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 130 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
23 | Lump15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_69 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 130 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
24 | Lump16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_40 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 330 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
25 | Lump13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_35 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
26 | Lump12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_34 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 300 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
27 | Lump11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_33 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 300 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
28 | Lump10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_32 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 50 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
29 | Lump8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_18 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 600 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
30 | Lump7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_17 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 300 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
31 | Lump4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_9 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 1560 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 10 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
32 | Lump2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_4 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 630 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
33 | Lump1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_3 | true | As-Built | 10 | 600 | Conventional | 80 | 100 | 300 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 50 | 6.67000008 | 25 | 16.666666 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
34 | Lump9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | true | As-Built | 10 | 650 | Conventional | 80 | 80 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50

## capacitor
Index | ID | OpMW | OpMvar | InService | InServiceState | InterDF | Phase | PhaseConnection | PdeStatus | CurrentLowerBand | CurrentSwitchInValue | CurrentSwitchOutValue | CurrentUpperBand | StepsPerBank | TimeDelayType | VoltageCtrlUnit | VoltageLowerBand | VoltageSwitchInValue | VoltageSwitchOutValue | VoltageUpperBand | FailureRate | MTTR | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | UnitLength

## mgset
Index | ID | KV | MVA | X1 | Xdu | Xq | XqP | XqPP | Xqu | FailureRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | UnitLength

## hvcb
Index | ID | FromElement | ToElement | FailureRate | MTTR | OutageRate | OutageTime | PermFailureRate | PdeStatus | ReplaceTime | SpareAvail | SwitchTime

## dcbus
Index | ID | InService | InServiceState | MaxLoadFactor | MinLoadFactor | NominalV | PhaseType | WireType | aCoefficient | FailureRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | UnitLength
1 | dcBus_1 | true | As-Built | 125 | 80 | 824 | 0 | 1 | 100 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | dcBus_2 | true | As-Built | 125 | 80 | 824 | 0 | 1 | 100 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | dcBus_3 | true | As-Built | 125 | 80 | 824 | 0 | 1 | 100 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## dcimpedance
Index | ID | FromBus | IID | InService | InServiceState | RValue | LValue | ToBus | PhaseType | WireType | FailureRate | MomentaryRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | UnitLength
1 | dcZ1 | dcBus_1 | 3222 | true | As-Built | 0.0599999987 | 0 | dcBus_2 | 0 | 1 | 0 | 80 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | dcZ2 | dcBus_3 | 3234 | true | As-Built | 0.0599999987 | 0 | dcBus_1 | 0 | 1 | 0 | 80 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## dclumpload
Index | ID | DCV | InService | InServiceState | KFactor | KW | MTLoadPercent | Bus | StaticLoadPercent | PhaseType | ProfileSector | SingleYearForecastOpt | FailureRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | UniformScalePQ

## dcconverter
Index | ID | IMaxPercent | InputBus | InputPhaseType | InputTerminalType | InputV | InService | InServiceState | KW | OutputBus | OutputPhaseType | OutputTap | OutputTerminalType | OutputV | PercentEFF | FailureRate | MTTR | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime

## dccb
Index | ID | FromBus | ToBus | FailureRate | MTTR | OutageRate | OutageTime | PdeStatus | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime

## inverter
Index | ID | OpAcKw | OpAcKvar | OpAcKv | OpAcAmp | OpDcKw | DckW | DcPercentEFF | DcPercentIMax | DcPhaseType | DcTerminalType | DcV | DcVMax | DcVMin | diDV | EarthingType | GenerationCategory | BusID | CZNetwork | IkPFMax | IkPFMin | IMin | InService | ParentName | InServiceState | KV | GenCat0ACkW | GenCat0kVar | KVA | KVAMax | KvarMax | KWMax | MaxPF | MinPF | MPPTControl | MPPTDCVMax | MPPTDCVMin | MPPTInitialDCV | MPPTNumSteps | MvarLimitsOpt | NegSeqCurrentInjection | NegSeqCurrentLimit | NegSeqDeadbandMin | NegSeqDiDV | PF | Phase | PhaseConnection | PowerFactorOpt | RegulatedVac | SmartInverterOpt | SP3Wire | SpareDF | StaticVarSupportPercentage | VAtIMax | VMaxOp | VMinOp | Vref | VShutOff | PdeStatus | FailureRate | MTTR | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | UserDefPoints
1 | Inv2 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 105 | 0 | 1 | 824 | 110 | 0 | 2 | 0 | IP8AAPP/AAAKAAAAAADIQgAAyEIAAAAAAADIQgAAAAAAAEhCAADIQgAAAAAAAAAAAAAAAAAAoEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAADAAAAAAAAAAAAVkAAAAAAAABZQAAAAAAAAFZAAAAAAAAAWUAAAAAAAIBaQAAAAAAAAFlAAAAAAACAWkAAAAAAAABZQAAAAAAAgFtAAAAAAAAANEAAAAAAAIBbQAAAAAAAADRAAAAAAA | Bus_20 | dcBus_1 | 110 | 100 | 100 | false |  | As-Built | 10 | 100 | 50 | 0 | 300 | 0 | 0 | 100 | 80 | 0 | 110 | 40 | 100 | 15 | 0 | 0 | 100 | 10 | 2 | 100 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 40 | 110 | 90 | 100 | 50 | Continuous | 1.254 | 5 | 1 | 8 | 1.254 | 10 | 0 | 2 | <UserDefPoints><UserDefPQPoints></UserDefPQPoints><UserDefPVPoints><UserDefPVPoint percentVGenerating="88.00" percentPGenerating="100.00" percentVCharging="88.00" percentPCharging="100.00" /><UserDefPVPoint percentVGenerating="106.00" percentPGenerating="100.00" percentVCharging="106.00" percentPCharging="100.00" /><UserDefPVPoint percentVGenerating="110.00" percentPGenerating="20.00" percentVCharging="110.00" percentPCharging="20.00" /></UserDefPVPoints><UserDefQVPoints></UserDefQVPoints></UserDefPoints>
2 | Inv1 | 0 | 0 | 0 | 0 | 0 | 300 | 90 | 105 | 0 | 1 | 824 | 110 | 0 | 2 | 5 | IP8AAPP/AAAKAAAAAADIQgAAyEIAAAAAAADIQgAAAAAAAEhCAADIQgAAAAAAAAAAAAAAAAAAoEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAADAAAAAAAAAAAAVkAAAAAAAABZQAAAAAAAAFZAAAAAAAAAWUAAAAAAAIBaQAAAAAAAAFlAAAAAAACAWkAAAAAAAABZQAAAAAAAgFtAAAAAAAAANEAAAAAAAIBbQAAAAAAAADRAAAAAAA | Bus_21 | dcBus_2 | 110 | 100 | 100 | true |  | As-Built | 10 | 100 | 50 | 270 | 270 | 270 | 270 | 100 | 80 | 0 | 110 | 40 | 100 | 15 | 0 | 0 | 100 | 10 | 2 | 100 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 40 | 110 | 90 | 100 | 50 | Continuous | 1.254 | 5 | 1 | 8 | 1.254 | 10 | 0 | 2 | <UserDefPoints><UserDefPQPoints></UserDefPQPoints><UserDefPVPoints><UserDefPVPoint percentVGenerating="88.00" percentPGenerating="100.00" percentVCharging="88.00" percentPCharging="100.00" /><UserDefPVPoint percentVGenerating="106.00" percentPGenerating="100.00" percentVCharging="106.00" percentPCharging="100.00" /><UserDefPVPoint percentVGenerating="110.00" percentPGenerating="20.00" percentVCharging="110.00" percentPCharging="20.00" /></UserDefPVPoints><UserDefQVPoints></UserDefQVPoints></UserDefPoints>
3 | Inv3 | 0 | 0 | 0 | 0 | 0 | 300 | 90 | 105 | 0 | 1 | 824 | 110 | 0 | 2 | 5 | IP8AAPP/AAAKAAAAAADIQgAAyEIAAAAAAADIQgAAAAAAAEhCAADIQgAAAAAAAAAAAAAAAAAAoEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAADAAAAAAAAAAAAVkAAAAAAAABZQAAAAAAAAFZAAAAAAAAAWUAAAAAAAIBaQAAAAAAAAFlAAAAAAACAWkAAAAAAAABZQAAAAAAAgFtAAAAAAAAANEAAAAAAAIBbQAAAAAAAADRAAAAAAA | Bus_22 | dcBus_3 | 110 | 100 | 100 | false |  | As-Built | 10 | 100 | 50 | 270 | 270 | 270 | 270 | 100 | 80 | 0 | 110 | 40 | 100 | 15 | 0 | 0 | 100 | 10 | 2 | 100 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 40 | 110 | 90 | 100 | 50 | Continuous | 1.254 | 5 | 1 | 8 | 1.254 | 10 | 0 | 2 | <UserDefPoints><UserDefPQPoints></UserDefPQPoints><UserDefPVPoints><UserDefPVPoint percentVGenerating="88.00" percentPGenerating="100.00" percentVCharging="88.00" percentPCharging="100.00" /><UserDefPVPoint percentVGenerating="106.00" percentPGenerating="100.00" percentVCharging="106.00" percentPCharging="100.00" /><UserDefPVPoint percentVGenerating="110.00" percentPGenerating="20.00" percentVCharging="110.00" percentPCharging="20.00" /></UserDefPVPoints><UserDefQVPoints></UserDefQVPoints></UserDefPoints>

## charger
Index | ID | OpMW | OpMvar | DckW | DcLoadkW | DcPercentIMax | DcPhaseType | DcSmoothL | DcSmoothR | DcTapPercentage | DcTerminalType | DcV | DcVeq | DcVFloat | DcVFloatMax | DcVFloatMin | IAtZeroV | IMin | InService | InServiceState | Iop | Issue | KV | KVA | MVA | Bus | CZNetwork | MVASc | OperatingAlfa | PercentDF | PercentEFF | Phase | PhaseConnection | ScContribution | ScK | SP3Wire | SpareDF | SystemR | SystemX | SystemXOverR | UpdateZFromSc | VAtIMax | Xc | XfmrR | XfmrX | PdeStatus | ProfileSector | RectifierMaxV | SCMaxV | SCMfrModelID | SCParameter | SCSpeed | SCStandard | FailureRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime

## battery
Index | ID | BatteryType | DisChargeMethod | Eff | IchargeMax | IdischargeMax | InService | InServiceState | Bus | NrOfCells | NoOfPacks | NrOfStrings | IValue | OperatingSoC | OpGenBusGID | OpGenBusID | OpGenChargeBand | OpGenChargeMW | OpGenDisChargeBand | OpGenDisChargeMW | PhaseType | QValue | Rated | TerminalType | VbatMax | VbatMin | FailureRate | MTTR | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | ModelID | ModelType
1 | Battery1 | 0 | 1 | 85 | 10 | 20 | true | As-Built | dcBus_3 | 20 | 20 | 20 | 0 | 0 | 2185560065 | 3220 | 0.00100000005 | 1 | 0.00100000005 | 0.100000001 | 0 | 110 | 1 | 1 | 120 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450043002D003200300030003700200020002000200020000000000000003041443730333430762F000030304330373934343030303030303030190008000000 | 050000000000484300005C4366463B440000CE440AD7233B